# ENERGIZED ELECTRICAL WORK PERMIT

PART I: TO BE COMPLETED BY THE REQUESTER:

Job Work Order Number:________________

- Description of circuit/equipment/job location:	HRC #2 Other    /

- Description of work to be done:
Diagnostic testing, including voltage testing

- Justification of why the circuit/equipment cannot be de-energized or the work deferred until the next scheduled outage:

___________________________		__________________________

Requester/Title					          Date

PART II: TO BE COMPLETED BY THE ELECTRICALLY QUALIFIED PERSONS DOING THE WORK:

- Detailed job description procedure to be used in performing the above described work:

- Description of the Safe Work Practices to be employed:

| Shock hazard: 0.48 kV | Shock Boundary: 1' - 0" | V-rated Gloves: Yes, Class 00 |
| --- | --- | --- |
| Flash Hazard: 7.9 cal/cm2 | Flash Boundary: 5' - 5" | V-rated Tools: Yes |
| HC Reduction: 0 | Required PPE: #2* | Work Distance: 1' - 6" |
| Arc rated (cal/cm2): clothing (long-sleeve shirt/pants or coveralls), face shield and head sock. Additional PPE: Hard hat (w/FR Liner), safety glasses, leather work shoes, ear canal inserts and dielectric gloves/leather protectors. |

- Means employed to restrict the access of unqualified persons from the work areas:

- Evidence of completion of a Job Briefing including discussion of any job-specific hazards:

See Attached Job Briefing Report

- Do you agree the above-described work can be done safely?

( Yes		( No (If no, return to requester)

__________________________________			___________________

Electrically Qualified Person(s)				                Date

__________________________________			___________________

Electrically Qualified Person(s)				                Date

PART III: APPROVAL(S) TO PERFORM THE WORK WHILE ELECTRICALLY ENERGIZED:

__________________________________		________________________________

Manufacturing Manager			    Maintenance/Engineering Manager

__________________________________		________________________________

Safety Manager				    Electrically Knowledgeable Person

__________________________________		________________________________

General Manager					            Date

Note: Once the work is complete, forward this form to the site Safety Department for review and retention.

### Job Briefing and Planning Checklist

#### Identify

(	What are the hazards?			(	Potential for arc flash

(	What voltage levels are involved?		(	Unusual work conditions

(	What skills are required?			(	Is this a multiple-person job?

- “Foreign” voltage source present?

#### Ask

(	Can the equipment be de-energized?	(	Is a “standby person” required?

- Are there possible backfeeds of the circuits to be worked on?

#### Check

(	Job Plans				(	Safety procedures

(	One lines and vendor prints		(	Vendor Information

(	Status Board				(	Individuals familiar with facility?

- For up-to-date information on plant and vendor resources

#### Know

- What is the job?				(	EasyPower one-line has been printed, reviewed, and attached to
						energized work permit?

- Who is in charge?

- Who else needs to know?…..Communicate!

#### Think

(	About the extra event…What if?		( 	Use the right tools and equipment, including PPE

(	Lock-Tag-Test-Try			(	Install barriers and barricades

(	Test for voltage – FIRST			(	What else…?

- Install and remove grounds

#### Prepare for an emergency

(	Standby person CPR trained		(	What is the exact work location?

(	Telephone location?			(	How is the equipment shut off in an emergency?

(	Fire alarm locations?			(	Where is the emergency equipment?

(	Confined space rescue available if required? 	(	Is the required emergency equipment available?

(	Emergency phone numbers?		(	Radio communications available?

(	Extinguisher?