## Sheet1
Energized work shall only be performed when permitted by Section 130.1(A)! For tasks not listed or for power systems with greater than the assumed maximum short circuit current capacity or with longer than the assumed maximum fault clearing times, an arc flash hazard analysis shall be required in accordance with 130.3. This summary Table is only for use by QUALIFIED PERSONNEL that have been trained in accordance with the most current version of NFPA 70E, Article 130.
Tasks Performed on Energized Equipment (600 volts of less)
Table A - Panelboards or Other Equipment Rated 240 V and Below — Note 1 |  |  | Table D - 600 V Class Motor Control Centers (MCCs) — Note 2 (except as indicated)
Perform infrared thermography and other non-contact inspections outside the restricted approach boundary | L | 0 | Perform infrared thermography and other non-contact inspections outside the restricted approach boundary | L | 1
Circuit breaker (CB) or fused switch operation with covers on | L | 0 | CB or fused switch or starter operation with enclosure doors closed | L | 0
CB or fused switch operation with covers off | L | 0 | Reading a panel meter while operating a meter switch | L | 0
Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 1 | CB or fused switch or starter operation with enclosure doors open | L | 1
Remove/install CBs or fused switches | G/T | 1 | Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 2*
Removal of bolted covers (to expose bare, energized electrical conductors and circuit parts) | L | 1 | Work on control circuits with energized electrical conductors and circuit parts 120 V or below, exposed | G/T | 0
Opening hinged covers (to expose bare, energized electrical conductors and circuit parts | L | 0 | Work on control circuits with energized electrical conductors and circuit parts >120 V, exposed | G/T | 2*
Work on energized electrical conductors and circuit parts of utilization equipment fed directly by a branch circuit of the panelboard | G/T | 1 | Insertion or removal of individual starter “buckets” from MCC — Note 3 | G | 4
Note 1. Maximum of 25 kA short circuit current available; maximum of 0.03 sec (2 cycle) fault clearing time. |  |  | Application of safety grounds, after voltage test | G | 2*
|  |  | Removal of bolted covers (to expose bare, energized electrical conductors and circuit parts) — Note 3 | L | 4
Table B - Panelboards or Switchboards Rated >240 V and up to 600 V (with molded case or insulated case circuit breakers) — Note 1 |  |  | Opening hinged covers (to expose bare, energized electrical conductors and circuit parts) — Note 3 | L | 1
Perform infrared thermography and other non-contact inspections outside the restricted approach boundary | L | 1 | Work on energized electrical conductors and circuit parts of utilization equipment fed directly by a branch circuit of the motor control center | G/T | 2*
CB or fused switch operation with enclosure doors closed | L | 0 | Note 2. Maximum of 65 kA short circuit current available; maximum of 0.03 sec (2 cycle) fault clearing time.
CB or fused switch operation with covers off | G | 1 | Note 3. Maximum of 42 kA short circuit current available; maximum of 0.33 sec (20 cycle) fault clearing time.
Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 2*
Work on energized electrical conductors and circuit parts of utilization equipment fed directly by a branch circuit of the panelboard or switchboard | G/T | 2* | Table E - 600 V Class Switchgear (with power circuit breakers or fused switches) — Note 4
Note 1. Maximum of 25 kA short circuit current available; maximum of 0.03 sec (2 cycle) fault clearing time. |  |  | Perform infrared thermography and other non-contact inspections outside the restricted approach boundary | L | 2
|  |  | CB or fused switch operation with enclosure doors closed | L | 0
Table C - Other 600 V Class (277 V through 600 V, nominal) Equipment — Note 2 (except as indicated) |  |  | Reading a panel meter while operating a meter switch | L | 0
Lighting or small power transformers (600 V, maximum) |  |  | CB or fused switch operation with enclosure doors open | L | 1
Removal of bolted covers (to expose bare, energized electrical conductors and circuit parts) | L | 2 | Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 2*
Opening hinged covers (to expose bare, energized electrical conductors and circuit parts) | L | 1 | Work on control circuits with energized electrical conductors and circuit parts 120 V or below, exposed | G/T | 0
Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 2* | Work on control circuits with energized electrical conductors and circuit parts >120 V exposed | G/T | 2*
Application of safety grounds, after voltage test | G | 2* | Insertion or removal (racking) of CBs from cubicles, doors open or closed | L | 4
Revenue meters (kW-hour, at primary voltage and current) Insertion or removal | G | 2* | Application of safety grounds, after voltage test | G | 2*
Cable trough or tray cover removal or installation | L | 1 | Removal of bolted covers (to expose bare, energized electrical conductors and circuit parts) | L | 4
Miscellaneous equipment cover removal or installation | L | 1 | Opening hinged covers (to expose bare, energized electrical conductors and circuit parts) | L | 2
Work on energized electrical conductors and circuit parts, including voltage testing | G/T | 2* | Note 4. Maximum of 35 kA short circuit current available; maximum of up to 0.5 sec (30 cycle) fault clearing time.
Application of safety grounds, after voltage test | G | 2*
Insertion or removal of plug-in devices into or from busways | G | 2* | *Table X - Hazard Risk Categories that are Known to be Extremely Dangerous
Note 2. Maximum of 65 kA short circuit current available; maximum of 0.03 sec (2 cycle) fault clearing time. |  |  | 480V Building Service Entrance Equipment | G/T | 4+
Author's Notes: |  |  | Equipment on the 480V/secondary side of a Ind/Comm substation | G/T | 4+
1. "G/T" indicates a requirement of insulated gloves, leather protectors and insulated tools. 2. "G": indicates a requirement of insulated gloves and leather protectors. 3. "L" indicates a requirement of leather gloves. |  |  | All equipment on the load side of circuit breakers containing a short-time delay setting. Temporary removal of short time-delay is recommended. | G/T | 4+
3.The third column in each table is the level of Hazard Risk. There are five Categories, 0 through 4. Zero being the least dangerous and four being the most dangerous. |  |  | *The above areas are known to commonly equal or exceed a HRC #4, calculations should be done prior to energized work
General Notes (applicable to the tasks that are 600 volts or less:
(a) Rubber insulating gloves are gloves rated for the maximum line-to-line voltage upon which work will be done.
(b) Insulated and insulating hand tools are tools rated and tested for the maximum line-to-line voltage upon which work will be done, and are manufactured and tested in accordance with ASTM F 1505, Standard Specification for Insulated and Insulating Hand Tools.
(d) For systems rated less than 1000 volts, the fault currents and upstream protective device clearing times are based on an 18 in. working distance.
(f) For equipment protected by upstream current limiting fuses with arcing fault current in their current limiting range (1⁄2 cycle fault clearing time or less), the hazard/risk category required may be reduced by one number