## Sheet1
Table CC.1
Control Transformer Overcurrent Protection - Recommended Fuse Sizes - Gould Type ATQR
| Transformer Primary | [7 empty] | Transformer Secondary
| Primary Fuse Block |  | 480 Volt |  |  | 240 Volt
Transformer | Class CC | [7 empty] | Full | Midget Fuse | Secondary Fuse Block
Rating |  |  | Recommended Fuse Type/Rating |  |  | Recommended Fuse Type/Rating |  |  | Load | Gould
Volt | Transformer | Panel | U.L. Class CC - Gould Type ATQR |  |  | U.L Class CC - Gould Type ATQR |  |  | Amps | Type
Amperes | Mount | Mount | [6 empty] | (f.l.a.) | TRM | Transformer | Panel
(VA) | 3-Pole | 2-Pole | Primary | Transformer | Fuse Type | Primary | Transformer | Fuse Type | @120 V |  | Mount | Mount
| Acme | Gould |  | Acme | Ferraz |  | Acme | Ferraz |  |  | Single Pole | Single Pole
|  |  | (Amps) | Part # | ATQR | (Amps) | Part # | ATQR |  |  | Acme | Ferraz
50 | Add F3 | 30323R | 0.10417 | TA-2-81210 | 0.3 | 0.20833 | TA-2-81210 | 0.6 | 0.41667 | TRM .5 | PL-112602 | 30321
75 | Add F3 | 30322R | 0.15625 | TA-2-81201 | 0.4 | 0.3125 | TA-2-81201 | 0.8 | 0.625 | TRM .75 | PL-112602 | 30321
100 | Add F3 | 30322R | 0.20833 | TA-2-81211 | 0.6 | 0.41667 | TA-2-81211 | 1.25 | 0.83333 | TRM 1 | PL-112602 | 30321
150 | Add F3 | 30322R | 0.3125 | TA-2-81212 | 0.8 | 0.625 | TA-2-81212 | 1.5 | 1.25 | TRM 1.6 | PL-112602 | 30321
250 | Add F3 | 30322R | 0.52083 | TA-2-81213 | 1.5 | 1.0417 | TA-2-81213 | 3 | 2.0833 | TRM 2.5 | PL-112601 | 30321
300 | Add F3 | 30322R | 0.625 | TA-2-81200 | 1.5 | 1.25 | TA-2-81200 | 3.5 | 2.5 | TRM 3.2 | PL-112601 | 30321
350 | Add F3 | 30322R | 0.72917 | TA-2-81214 | 2 | 1.4583 | TA-2-81214 | 4 | 2.9167 | TRM 3.5 | PL-112601 | 30321
500 | Add F3 | 30322R | 1.0417 | TA-2-81215 | 3 | 2.0833 | TA-2-81215 | *5.0 | 4.1667 | TRM 5 | PL-112601 | 30321
750 | Add F3 | 30322R | 1.5625 | TA-2-81216 | 4.5 | 3.125 | TA-2-81216 | *7.0 | 6.25 | TRM 8 | PL-112601 | 30321
1000 | Add F3 | 30322R | 2.0833 | TA-2-81217 | *5.0 | 4.1667 | TA-2-81217 | *10.0 | 8.3333 | TRM 10 | PL-112601 | 30321
1500 | Add F3 | 30322R | 3.125 | TA-2-81218 | *7.0 | - | - | - | 12.5 | TRM 15 | PL-112601 | 30321
2000 | Add F3 | 30322R | 4.1667 | TA-2-81219 | *10.0 | - | - | - | 16.6667 | TRM 20 | PL-112601 | 30321
* The National Electrical Code Section 450-3 (600 Volt rules) allows transformer protection with only a primary fuse (Primary-Only Rule), although allowed this practice is not recommended. The asterisks indicates where secondary protection is required by the NEC rules.
Note! The suffix "F3" must be added to the Acme Transformer Part number to obtain the integral mount fuse block. This block includes two primary fuses (Class CC) and one secondary fuse (Midget Class)