# SECTION 16060 – GROUNDING AND BONDING

PART 1 - GENERAL

1.1		RELATED DOCUMENTS

A.	Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

B.	Division 16 Section "Basic Electrical Materials and Methods" shall apply to work specified  in this section.

C.	Requirements of this section apply to electrical grounding and bonding work specified elsewhere in these specifications.

1.2		SUMMARY

A.	This Section includes:

1.	Grounding of electrical systems and equipment and basic requirements for grounding for protection of life, equipment, circuits, and systems.

2.	Building Ground Rings (counterpoise systems)

B.	Provide grounding of the entire electrical installation as shown on the Drawings and specified herein, and in accordance with Article 250 of the National Electrical Code (NEC).

C.	Grounding requirements specified in this Section may be supplemented in other Sections of these Specifications.

1.3		SUBMITTALS

A.	General:  Submit each item in this Article according to the Conditions of the Contract and Division 1 Specification Sections.

B.	Product Data for grounding rods, connectors and connection materials, and grounding fittings.

C.	Field tests and observation reports certified by the testing organization and indicating and interpreting the test reports for compliance with performance requirements.

D.	Manufacturer’s instructions for storage, handling, protection, examination, preparation and installation of exothermic connectors.

1.4		QUALITY ASSURANCE

- A.	Testing Agency Qualifications:  Testing agency as defined by OSHA in 29 CFR 1910.7 or a member company of National Electrical Testing Association  (NETA)and that is acceptable to authorities having jurisdiction.

- Comply with UL 467.

- Listing and Labeling:  Provide products specified in this Section that are listed and labeled.

- Comply with NECA’s "Standard of Installation.”

PART 2 - PRODUCTS

2.1		GROUNDING CONDUCTORS

A.	Governing Requirements:  Where types, sizes, ratings, and quantities indicated are in excess of National Electrical Code (NEC) requirements, the more stringent requirements and the greater size, rating, and quantity indications govern.

B.	Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1.	Erico Inc.; Electrical Products Group.

- ILSCO.

- Utilco.

C.	Wire and Cable Grounding Conductors

1.	Conform to NEC Table 8, except as otherwise indicated, for conductor properties, including stranding.

- Use only copper wire for both insulated and bare grounding conductors in direct contact with earth, concrete, masonry, crushed stone, and similar materials.

- Equipment Grounding Conductors:  Insulated with green color insulation.

4.	Grounding-Electrode Conductors:  Bare Stranded copper.

5.	Underground Conductors:  Bare, tinned, stranded, except as otherwise indicated.

6.	Bare Copper Conductors:  Conform to the following:

a.	Solid Conductors:  ASTM B 3.

b.	Assembly of Stranded Conductors:  ASTM B 8.

- c..	Tinned Conductors:  ASTM B 33.

- 7.	Copper Bonding Conductors:  As follows:

            - Bonding Cable:  28 kcmil, 14 strands of No. 17 AWG copper conductor, ¼ inch in diameter.

            - Bonding Conductor:  No. 4 or No. 6 AWG, stranded copper conductor.

            - Bonding Jumper:  Bare copper tape, braided bare copper conductors, terminated with copper ferrules; 1-5/8 inches wide and 1/16 inch thick.

            - Tinned Bonding Jumper:  Tinned-copper tape, braided copper conductors, terminated with copper ferrules; 1-5/8 inches wide and 1/16 inch thick.

- Ground Conductor and Conductor Protector for Wood Poles:  As follows:

            - No. 4 AWG minimum, soft-drawn copper conductor.

            - Conductor Protector:  Half-round PVC or wood molding.  If wood, use pressure-treated fir, or cypress or cedar.

9.	Grounding Bus:  Bare, annealed-copper bars of rectangular cross section, with insulators.

10.	Braided Bonding Jumpers:  Copper tape, braided No. 30 AWG bare copper wire, terminated with copper ferrules.

11.	Bonding Straps:  Soft copper, 0.05 inch thick and 2 inches wide, except as indicated.

D.	Connector Products

1.	Products shall be listed and labeled as grounding connectors for the materials used. No aluminum materials shall be utilized within 18” of the earth where used for the purpose of grounding.

- 2.	Compression connectors shall be type CRA as manufactured by Ilsco.

3.	Mechanical connectors shall be type SLUH as manufactured by Ilsco unless otherwise noted.

4.	Exothermic-Welded Connections shall be as manufactured by Erico.  Provide exothermic welding system for use in making electrical grounding connections of  copper  to  copper  or copper to steel.. Exothermically welded connections are required on all grounding electrode conductors, all connections to building steel (connections to structural member), all grounding conductors run under the earth, connection to ground rods and in any case where grounding conductors are subject to a hostile environment.

a.	The exothermic welding system furnished under these specifications shall meet the  applicable  requirements  of IEEE-80, Chapter  9,  Section  of  conductors  and  joints.

b.	Molds shall be made from graphite or other material that is so  designed  to provide an average life of not less than 50 exothermic welds under normal conditions. Molds shall bear permanent marking, indicating the name  of  the manufacturer, the mold model,  the  type  and  size  of welding mixture compatible with the welding process, and the size of  the  conductor. Instructions  detailing  general safety information, and welding procedures shall be provided with each mold.

c.	Starting material, if used, shall consist of  aluminum  and copper/copper oxide  and iron oxides.  It shall not contain phosphorous or any caustic, toxic or explosive substance.  Weld metal used for grounding connections shall contain copper oxide, aluminum. Where welding is done in enclosed  structures, the Erico Exolon smokeless system shall be used.

E.	Grounding Electrodes and Test Wells

1.	Grounding Rods:  copper-clad steel, Size: 3/4 inch by 10 feet.

2.	Test Wells shall be type T416C as manufactured by Erico. Where multiple connection are made,  an Erico bus bar system, compression connectors and ground inspection well type T416A shall be used.

2.2		SIGNAL REFERENCE GRID (SRG)

A.	All raised floors shall utilize a signal reference grid as manufactured by Erico for  attenuation of high frequency interference.

- B.	The Signal Reference Grid shall be manufactured from 2 inch wide by No. 26 gauge (0.0159 inch thick) copper strips on 2 foot centers.

C.	The SRG shall be furnished in sections that can be placed by no more than two men. The sections shall be bonded together in the field with exothermic connections. All conductive raceways, members and equipment within the floor area shall be attached to the SRG with exothermic connections.. All equipment cabinets above the floor shall be attached to the SRG with a low impedance equipment riser (LIR)

PART 3 - EXECUTION

3.1		EXAMINATION

A.	Examine areas and conditions under which electrical grounding and bonding connections are to be made and notify the Engineer in writing of conditions detrimental to proper completion of work.  Do not proceed with work until unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

3.2		APPLICATION

- A.	In raceways, use insulated equipment grounding conductors.

        - Exothermic-Welded Connections only: shall be used for connections to structural steel, ground rods, signal reference grid,  counterpoise conductors and for all underground connections, except those at test wells.

        - Equipment Grounding Conductor Terminations:  Use Ilsco type CRA compression connectors.

        - Ground Rod Clamps at Test Wells shall be Ilsco type GRC 68 as manufactured by Ilsco. Where a ground well consists of multiple connection points  a low impedance ground bus shall be utilized and the optional ground inspection well shall be installed.

E.	Edit below to suit Project.

        - Underground Grounding Conductors:  Use copper conductor, No. 2/0 AWG minimum.  Bury at least 30 inches below grade or bury 12 inches above duct bank when installed as Part of the duct bank.

- F.	Equipment Grounding Conductors:  Comply with NEC Article 250 for types, sizes, and quantities of equipment grounding conductors, except where specific types, larger sizes, or more conductors than required by NEC are indicated.

1.	Install equipment grounding conductor with circuit conductors for the items below in addition to those required by Code:

a.	Feeders and branch circuits.

b.	Lighting circuits.

c.	Receptacle circuits.

d.	Single-phase motor or appliance branch circuits.

e.	Three-phase motor or appliance branch circuits.

f.	Flexible raceway runs.

g.	Armored and metal-clad cable runs.

2.	Air-Duct Equipment Circuits:  Install an equipment grounding conductor to duct-mounted electrical devices operating at 120 V and above, including air cleaners and heaters.  Bond conductor to each unit and to air duct.

3.	Water Heater, Heat-Tracing, and Anti-frost Heater Circuits:  Install a separate equipment grounding conductor to each electric water heater, heat-tracing assembly, and anti-frost heating cable.  Bond conductor to heater units, piping, connected equipment, and components.

4.	Separately Derived Systems:  Where NEC requires grounding, ground according to NEC Paragraph 250-30.

G.	Connections to Lightning Protection System:  Bond grounding conductors, including grounding-conductor conduits, to lightning protection down conductors or lightning protection grounding conductors in compliance with NFPA 780.

H.	Common Ground Bonding with Lightning Protection System:  Bond electric power system, grounding electrode system  directly to lightning protection system earth connection at closest point to electric service grounding electrode.  Use bonding conductor sized same as system grounding conductor and install in conduit.

3.3		COUNTERPOISE

- Provide a ground ring conductor (counterpoise) extending around the perimeter of the building. . Bury counterpoise not less than 30 inches below grade and 10 feet from building foundation.  Use tinned-copper conductor not less than No. 2/0 AWG for counterpoise and for the tap to building steel. The counterpoise conductor trench shall be filled with 1” of Erico G.E.M. above and below the conductor.

- Ground the steel framework of the building with a  ground rod at every corner column and at every other exterrior column. The ground rods shall be located in the counterpoise trench  and shall be attached to the counterpoise with a type GY (conductor-to-rod) connection by Erico and  a XB (conductor-to-conductor) connection  by Erico. The top of the ground rod shall not be less than 24” below grade. The conductor that attaches the rod to the counterpoise shall run continuous to the base of the structural steel column and welded to the column.

3.4		INSTALLATION

A.	General:  Ground electrical systems and equipment according to NEC requirements, except where Drawings or Specifications exceed NEC requirements.

B.	Ground Rods for service entrance earth connection:  Install at least three rods spaced at least one-rod length from each other and located at least the same distance from other grounding electrodes.

1.	Drive ground rods until tops are 6 inches below finished floor or final grade, unless otherwise indicated.

2.	Interconnect ground rods with grounding-electrode conductors.  Use exothermic welds, except at test wells and as otherwise indicated.  Make connections without exposing steel or damaging copper coating.

3.	Where soil conditions make driving ground rods impossible, a six inch hole shall be augured into the earth and filled with Erico Gem after the ground rod connection is made, or a trench no less than 24’ deep shall be utilized for horizontal placement of the rod. and backfilled with Erico Gem.

C.	Grounding Conductors:  Route along the shortest and straightest paths possible, unless otherwise indicated. Avoid obstructing access or placing conductors where they may be subjected to strain, impact, or damage.

- D.	Bonding Straps and Jumpers:  Install so vibration by equipment mounted on vibration isolation hangers and supports is not transmitted to rigidly mounted equipment.  Use exothermic-welded connectors for outdoor locations, unless a disconnect-type connection is required; then, use a bolted clamp.  Bond straps directly to the basic structure taking care not to penetrate any adjacent parts.  Install straps only in locations accessible for maintenance.

E.	Metal Water Service Pipe:  Provide insulated copper grounding conductors, sized as indicated, in conduit, from building's main service equipment, or grounding bus, to main metal water service entrances to building. Connect grounding conductors to main metal water service pipes by grounding-clamp connectors.  Where a dielectric main water fitting is installed, connect grounding conductor to street side of fitting.  Do not install a grounding jumper across dielectric fittings.  Bond grounding-conductor conduit to conductor at each end.

- Water Meter Piping:  Use braided-type bonding jumpers to electrically bypass water meters.  Connect to pipe with grounding-clamp connectors.

- Bond interior metal piping systems and metal air ducts to equipment grounding conductors of associated pumps, fans, blowers, electric heaters, and air cleaners.  Use braided-type bonding straps.

H.	Bond each aboveground portion of gas piping system upstream from equipment shutoff valve.

I.	Test Wells:  One for each service at the ground rod electrically closest to the service entrance.  Set top of well flush with finished grade or floor.  Fill with 1-inch maximum-size crushed stone or gravel.

3.5		CONNECTIONS

A.	General:  Make connections so possibility of galvanic action or electrolysis is minimized.  Select connectors, connection hardware, conductors, and connection methods so metals in direct contact will be galvanically compatible.

1.	Use electroplated or hot-tin-coated materials to assure high conductivity and to make contact points closer in order of galvanic series.

2.	Make connections with clean, bare metal at points of contact.

3.	Make aluminum-to-steel connections with stainless-steel separators and mechanical clamps.

4.	Make aluminum-to-galvanized steel connections with tin-plated copper jumpers and mechanical clamps.

5.	Coat and seal connections having dissimilar metals with inert material to prevent future penetration of moisture to contact surfaces.

B.	Exothermic-Welded Connections:  Use for connections to structural steel and for underground connections, except those at test wells.  Comply with manufacturer's written instructions.  Welds that are puffed up or that show convex surfaces indicating improper cleaning are not acceptable.

C.	Equipment Grounding-Wire Terminations:  For No. 8 AWG and larger, use pressure-type grounding lugs, SLUH  type as manufactured by Ilsco. No. 10 AWG and smaller grounding conductors may be terminated with winged pressure-type connectors.

D.	Non-contact Metal Raceway Terminations:  Where metallic raceways terminate at metal housings without mechanical and electrical connection to housing, terminate each conduit with a grounding bushing.  Connect grounding bushings with a bare grounding conductor to grounding bus or terminal in housing.  Bond electrically noncontinuous conduits at both entrances and exits with grounding bushings and bare grounding conductors, except as otherwise indicated.

E.	Connections at Test Wells:  Use compression-type connectors on conductors and make bolted- and clamped-type connections between conductors and grounding rods.

F.	Tighten screws and bolts for grounding and bonding connectors and terminals according to manufacturer's published torque-tightening values.  Where these requirements are not available, use those specified in UL 486A and UL 486B.

G.	Compression-Type Connections:  Use hydraulic compression tools to provide correct circumferential pressure for compression connectors.  Use tools and dies recommended by manufacturer of connectors.  Provide embossing die code or other standard method to make a visible indication that a connector has been adequately compressed on grounding conductor.

H.	Moisture Protection:  Where insulated grounding conductors are connected to grounding rods or grounding buses, insulate entire area of connection and seal against moisture penetration of insulation and cable.

3.6		OVERHEAD LINE GROUNDING

A.	Comply with IEEE C2 requirements.  Use 2 or more parallel ground rods if a single ground rod electrode resistance to ground exceeds 25 ohms.

B.	Drive ground rods to a depth of 12 inches below finished grade in undisturbed earth.

C.	Ground Rod Connections:  Use clamp-type connectors listed for the purpose for underground connections and connections to rods.

D.	Lightning Arresters:  Separate arrester grounds from other grounding conductors.

E.	Secondary Neutral and Tank of Transformer:  Interconnect and connect to grounding conductor.

F.	Protect grounding conductors running on surface of wood poles with molding manufactured for this purpose. Extend from grade level up to and through communication service and transformer spaces.

3.7		UNDERGROUND DISTRIBUTION SYSTEM GROUNDING

        - Duct Banks:  Install a grounding conductor with at least 50 percent ampacity of the largest phase conductor in the duct bank.

B.	Manholes and Handholes:  Install a driven ground rod close to wall and set rod depth so 4 inches  will extend above finished floor.  If necessary, install ground rod before manhole is placed and provide a No. 1/0 AWG bare, tinned-copper conductor from ground rod into manhole through a waterproof sleeve in manhole wall. Protect ground rods passing through concrete floor with a double wrapping of pressure-sensitive tape or heat-shrunk insulating sleeve from 2 inches above to 6 inches below concrete.  Seal floor opening with waterproof, non-shrink grout.

C.	Connections to Manhole Components:  Connect exposed metal parts, such as inserts, cable racks, pulling irons, ladders, and cable shields within each manhole or handhole, to ground rod or grounding conductor. Make connections with minimum No. 4 AWG stranded, hard-drawn copper conductor.  Train conductors level or plumb around corners and fasten to manhole walls.  Connect to cable armor and cable shields as recommended by manufacturer of splicing and termination kits.

- Pad-Mounted Transformers and Switches:  Install four  ground rods and counterpoise circling pad.  Ground pad-mounted equipment and noncurrent-carrying metal items associated with substations by connecting them to underground cable and grounding electrodes.  Use tinned-copper conductor not less than No. 2 AWG for counterpoise and for taps to equipment ground pad.  Bury counterpoise not less than 18 inches below grade and 6 inches from the foundation. The pad rebar shall be attached to the counterpoise conductor at the four corners.

3.9		FIELD QUALITY CONTROL

A.	Independent Testing Agency:  Engage an independent electrical testing organization to perform tests described below.

B.	Tests:  Subject the completed grounding system to a megger test at each location where a maximum ground-resistance level is specified, at service disconnect enclosure grounding terminal, and at ground test wells.  Measure ground resistance not less than 2 full days after the last trace of precipitation, and without the soil being moistened by any means other than natural drainage or seepage and without chemical treatment or other artificial means of reducing natural ground resistance.  Perform tests by the 2-point method according to IEEE 81.

C.	The maximum earth resistance values shall be less than 5 ohms for the service entrance ground with the counterpoise removed and no greater for the counterpoise system when measured alone. Earth resistance testing shall be done no sooner than 180 days after occupancy and  prior to 360 days. Earth resistance testing shall be done by the done by the manufacturer of the earthing/grounding components and shall be included in the cost of materials.

D.	Excessive Ground Resistance:  Where resistance to ground exceeds specified values, notify Owner promptly and include recommendations to reduce ground resistance and to accomplish recommended work.

E.	Report:  Prepare test reports, certified by the testing organization, of ground resistance at each test location. Include observations of weather and other phenomena that may affect test results.  Describe measures taken to improve test results.

3.10	GRADING AND PLANTING

        - Restore surface features, including vegetation, at areas disturbed by work of this Section.  Reestablish original grades, except as otherwise indicated.  Where sod has been removed, replace it as soon as possible after backfilling is completed.  Restore areas disturbed by trenching, storing of dirt, cable laying, and other activities to their original condition.  Include topsoiling, fertilizing, liming, seeding, sodding, sprigging, and mulching.

        - Comply with other divisions of this specification.  Maintain restored surfaces.  Restore disturbed paving as required.

END OF SECTION 16060