MGE UPS SYSTEMS

GALAXY 3000 10-30 kVA UPS

Data Center Grade Three Phase Uninterruptible Power Supply

Guide Specifications
1.0  
GENERAL
1.1
SUMMARY

This specification describes a three phase, on-line, double conversion, solid state Uninterruptible Power System here after referred to as the UPS.  The UPS shall operate in conjunction with the existing building electrical system to provide high quality power conditioning, back-up power protection and distribution for electronic equipment loads. The system shall consist of a solid state inverter, power factor corrected rectifier/battery charger, a 100% rated for continuous duty static switch, an internal maintenance bypass switch, battery plant, graphical status/control panel, and synchronizing circuitry as described herein.

1.2 STANDARDS


The UPS shall meet the requirements of the following standards:

· IEEE 587-1980/ANSI C62.41 1980 Standards for Surge Withstand Ability

· FCC rules and regulations of Part 15, Subpart J, Class A

· UL listed under 1778, Standards for Uninterruptible Power Supply Equipment

· UL Canada (cUL)

· NEMA PE 1 (National Electrical Manufacturers Association) - Uninterruptible Power Systems

· NEMA 250  (National Electrical Manufacturers Association) – Enclosures for Electrical Equipment (1000 Volts Maximum)

· NFPA 70 – National Electrical Code

· ISO 9001

· Occupational Safety & Health Administration (OSHA)

1.3 SUBMITALS

Submittals shall contain the following documentation: 

A. Installation Drawings: Indicate electrical characteristics and connection requirements.  Provide cabinet dimensions; battery type, size, dimensions, and weight; detailed equipment outlines, weight, and dimensions; location of conduit entry and exit; single-line diagram, control, and external wiring requirements; heat rejection and air flow requirements.

B. Product Data: Provide catalog sheets and technical data sheets to indicate physical data and electrical performance, electrical characteristics, and connection requirements.

C. Manufacturer’s Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.  Include equipment installation outline, connection diagram for external cabling, internal wiring diagram, and written instruction for installation.

1.4 FINAL SUBMITALS

Upon delivery of the UPS system the following submittals shall be included:

A. A completed set of installation drawings showing all the information stated in section 1.3

B. An operators and users manual showing safe and correct operation of all UPS functions.

1.5 QUALIFICATIONS & QUALITY ASSURANCE

Manufacturers Certification: The manufacturer shall specialize in manufacturing of on-line, double conversion three phase UPS modules specified in this document with a minimum of twenty years documented experience, and with a nation wide first party service organization. The manufacturer shall be ISO 9001 certified and shall design to internationally accepted standards.

Factory Testing: Prior to shipment the manufacturer shall complete a documented test procedure to test all functions of the UPS module and batteries (via a discharge test) when supplied by the UPS manufacturer and guarantee compliance with the specification.  The factory test shall be performed in the presence of the customer providing the manufacturer receives adequate prior notice.  The manufacturer shall provide a copy of the test report upon request. 

Materials and Assemblies: All materials and parts comprising the UPS shall be new, of current manufacture, and shall not have been in prior service, except as required during factory testing.  All active electronic devices shall be solid state and not exceed the manufacturers recommended tolerances for temperature or current to ensure maximum reliability. All semiconductor devices shall be sealed. All relays shall be provided with dust covers.  The manufacturer shall conduct inspections on incoming parts, modular assemblies and final products.

1.6 DELIVERY, STORAGE, AND HANDLING

A. All products shall be packaged in a manner to prevent penetration by debris and to allow safe delivery by all modes of ground transportation and air transportation where specified.

B. Prior to shipping all products shall be inspected at the factory for damage. 

C. Equipment shall be protected against extreme temperature and humidity and shall be stored in a conditioned or protected environment. 

D. Equipment containing batteries shall not be stored for a period exceeding three months without powering up the equipment for a period of eight hours to recharge the batteries. 

1.7 ENVIRONMENTAL REQUIREMENTS

The UPS shall operate under the following environmental conditions:

A. Temperature:



UPS Module Operating: 
 0° to 40°C (32°F to 105°F) 




Batteries: 

 
25°C (77°F) 


Non-Operating:


-20°C to +70°C (-4°F to 158°F)  

B. Relative humidity (operating and storage):  0 to 95% non-condensing

C. Barometric Pressure:  Up to 1000 meters above sea level (up to 2000 meters with ambient temperature less than 28°C) / (up to 12,000 meters above sea level non operating)

D. Audible  Noise:
 52-55 dBA at 3 feet

1.8 WARRANTY

A. UPS Module: The UPS shall be covered by a full parts and labor warranty from the manufacturer for a period of twelve (12) months from date of installation or acceptance by customer or eighteen (18) months from date of shipment from the manufacturer, whichever occurs first.

B. Battery: The battery manufacturer’s warranty shall be passed through to the final customer and shall have a minimum period of one year.  
1.9
SERVICE AND SPARES PARTS

The manufacturer shall upon request provide spare parts kits for the UPS module in a timely manner as well as provide access to qualified factory trained first party service personnel to provide preventative maintenance and service on the UPS module when required. 

1.10
MAINTENANCE, ACCESABILITY AND SELF DIAGNOSTOCS
All UPS subassemblies, as well as the battery, shall be accessible from the front. UPS design shall provide maximum reliability and minimum MTTR (mean time to repair). To that end, the UPS shall be equipped with a self-test function to verify correct system operation. The self-test function shall identify the subassembly-requiring repair in the event of a fault. The electronic UPS control and monitoring assembly shall therefore be fully microprocessor based, thus doing away with all potentiometer settings. This shall allow:

( Auto-compensation of component drift;

( Self-adjustment of replaced subassemblies;

( Extensive acquisition of information vital for computer-aided diagnostics (local or remote);

( A socket for connection to a computer-aided diagnostics system.

The UPS shall be repairable by replacing standard subassemblies requiring no adjustments or settings. Communication via a modem with a remote maintenance system shall be possible. 
2.0  
PRODUCT DESCRIPTION

2.1 APPROVED MANUFACTURERS & PRODUCT DESCRIPTION

A. Approved Manufacturer(s): The specified equipment will be manufactured by MGE UPS SYSTEMS or approved manufacture in compliance with specifications

B. Product Description: This specification describes a three phase, double conversion, on-line, solid state Uninterruptible Power System here after referred to as the UPS.  The UPS shall operate in conjunction with the existing building electrical system to provide power conditioning, back-up power protection and distribution for electronic equipment loads. The system shall consist of a solid state IGBT PWM inverter, IGBT rectifier/battery charger with a power factor corrected input, static switch, internal maintenance bypass switch, battery plant, graphical status/control panel, dry contact and communications ports, and synchronizing circuitry as described herein. 
2.2
SYSTEM DESCRIPTION

A. UPS Design Requirements

1. Output Power Continuous Rating: The continuous output power rating of the UPS shall be shall be [      ] kVA at a 0.8 lagging power factor. 

2. Field Power Upgrade: The following power ratings may be upgraded in the field to provide up to 50% (fifty percent) more output power with no increase in footprint:

i) 10 kVA/8 kW UPS modules shall upgrade to 15 kVA/12 kW

ii) 20 kVA/16 kW UPS modules shall upgrade to 30 kVA/24 kW

3. Input Voltage:  [       ] VAC – 25% / +15%, 3 phase, 4 wire plus ground.

4. Output voltage: [      ] VAC 3 phase, 4 wire plus ground. 

5. Battery Autonomy:  The UPS shall be capable of operating at full load for [     ] minutes at 0.8 PF output at a temperature of 25°C on battery power. 
6. Battery Type: Valve regulated sealed lead acid (VRLA). 
B. AC Input Characteristics

1. Input Frequency: 60 Hz  (- 25% to + 15% )

2. Maximum Input Current  at Low Line Voltage: [       ] A

3. Input Power Factor:  > .98 lagging 

4. Harmonic Distortion of Input Current Wave Form: less than 3% at full load.

5. Power walk-in:  0 to 100% over a 10-second period.

6. Magnetizing Inrush Current: Less than nominal input current for less than one cycle.

7. Input Surge Protection: The UPS is equipped with input MOVs to withstand surges per IEEE 587-1980/ANSI C62.41

C. AC Output Characteristics

1. Voltage Regulation:   + 1.0% for balanced load; + 1.75 for 50% unbalanced load; + 2.5% for 100% unbalanced load

3. Frequency: 60 Hz +1% (or selectable up to 4% ). 60 Hz + 0.1% when free running. 

4. Voltage Distortion: Maximum 2% total (THD) and 1% any single harmonic on 100% linear loads.

5.
Voltage Transient (Step Load) Response:


+ 3% for 50% step load change 


+ 5% for 100% step load change


+ 1% for loss or return of AC input power or manual transfer at full load.

6. Voltage Recovery Time: Return to within 1% of nominal value within 16.67 milliseconds (one cycle).

7.
Phase Angle Displacement: 120° + 1° degrees for balanced load; 120° + 3° degrees for 100% unbalanced load

8. Non-Linear Load Capability: Output voltage total harmonic distortion shall be less than 3% when connected to a 100% non-linear load with a crest factor not to exceed 3%.

9. Slew Rate: 1 Hz/second maximum (or selectable up to 2.0 Hz/sec).

10.
Power Factor:  0.8 at the rated volt-amperes (VA)

11.
Inverter Overload Capability: 



120% of rated load for 1 minute



145% of rated load for 30 seconds

12. Bypass Overload Capability: > 212% for one cycle; > 150% for 30 seconds

D. DC Bus 

1. DC Bus Voltage: 198 VDC minimum before cutout; 240 VDC nominal, 277 VDC maximum maintenance charge voltage; 300 VDC equalization voltage
2.
Maximum DC Current:  Maximum DC current at cutoff voltage will be [        ] A.

2.3
MODES OF OPERATION

The UPS module shall be designed to operate as a double conversion, on-line reverse transfer system in the following modes.

2.3.1 Normal: The inverter shall continuously supply power to the critical load.  The rectifier/battery charger shall derive power from the utility AC source and supply DC power to the inverter while simultaneously float charging the battery.

2.3.2 Emergency: Upon failure of the utility AC power source, the critical load shall be supplied by the inverter, which, without any switching, shall obtain its power from the battery.

2.3.3 Recharge:  Upon restoration of the utility AC power source (prior to complete battery discharge), the rectifier/battery charger shall power the inverter and simultaneously recharge the battery.

2.3.4 Bypass Mode: 
The static bypass transfer switch shall be used to transfer the load to the bypass without interruption to the critical power load.  This shall be accomplished by turning the inverter off.  Automatic re-transfer or forward transfer of the load shall be accomplished by turning the inverter on.

2.3.5 Maintenance Bypass/Test Mode: A manual make before break internal maintenance bypass switch shall be provided to isolate the UPS inverter output and static bypass transfer switch for maintenance.  This shall allow the UPS to be tested or repaired without affecting load operation.

2 COMPONENT DESCRIPTION

2.4.1  Rectifier / Battery Charger

Incoming AC power shall be converted to a regulated DC output voltage by an IGBT (insulated gate bipolar transistor) power factor corrected  (PFC) rectifier rectifier/battery charger. The rectifier / battery charger shall provide high quality DC power to charge the batteries and power the inverter and shall have the following characteristics: 
A. Input Power Factor Correction (PFC): The rectifier shall be power factor corrected so as to maintain an input power factor of 0.98 lagging to unity at all load levels to ensure generator compatibility and avoid reflected harmonics from disturbing loads sharing the utility power. 

B. Input Harmonic Current Suppression: The PFC rectifier/battery charger shall produce a sinusoidal input AC current on each phase with low harmonic content, limiting THD on the UPS input to below 3%. This shall eliminate the requirement for an input filter. 
C. Input Current Limiting: The UPS shall be equipped with a system designed to limit the battery recharge current (from 0.05 C10 to 0.1 C10).
D. Modular Assembly: The rectifier/battery charger assembly shall be constructed of modular design to facilitate rapid maintenance. 

E. Charging Levels: The battery charging circuitry shall be capable of being set for automatic battery recharge operation, float service, manual battery charge service and equalizing or commissioning operation. 

F. Intermittent Charging: The battery charge level shall be maintained by an intermittent charging technique between two values Vfmin and Vfmax very close to the floating voltage. This technique shall be based on a cycle made up of a short charge period (a few seconds) from Vfmin to Vfmax followed automatically by a slow discharge period (a few minutes) from Vfmax to Vfmin. This cycle shall be repeated continuously to maintain the battery charge level. In this way the battery shall actually be charging only for a small part of the time, which considerably increases its service life. 

G. Temperature Compensated Charging: The battery charger shall be equipped with a temperature probe to enable temperature compensated charging and adjust the battery float voltage to compensate for the ambient temperature using a negative temperature coefficient of 3 mV per cell per degree Celsius at a nominal temperature of 25°C. 

H. Capacity: The rectifier/battery charger shall have sufficient capacity to support a fully loaded inverter and fully recharge the battery to 95% of its full capacity within 6-8 hours.
1.4.2 Inverter

The UPS output shall be derived from a Pulse Width Modulated (PWM) IGBT inverter design. The inverter shall be capable of providing the specified precise output power characteristics (specified in section 2.2.C) while operating over the battery voltage range.  The inverter assembly shall be constructed as a modular assembly to facilitate rapid maintenance.

2.4.3 Static Bypass

The static bypass transfer switch shall be solid-state, rated for continuous 100% duty and shall operate under the following conditions:

A. Uninterrupted Transfer:  The static bypass transfer switch shall automatically cause the bypass source to assume the critical load without interruption after the logic senses one of the following conditions:

1) Inverter overload exceeds unit's rating

2) Battery protection period expired and bypass current is available

3) Inverter failure

B. Interrupted Transfer: If the bypass source is beyond the conditions stated below, the UPS will make an interrupted transfer (not less than 500 msec. in duration).

1) Bypass voltage greater than + 10%, -10% from the UPS rated output voltage.

2) Bypass frequency greater than + 2 Hz from the UPS rated output frequency.

C. Automatic Uninterrupted Forward Transfer: The static bypass transfer switch shall automatically forward transfer power from the bypass to the rectifier / inverter, without interruption, after the UPS inverter is turned "ON", after an instantaneous overload-induced reverse transfer has occurred and the load current returns the UPSs nominal rating or less. 

D. Manual Transfer: A manual static transfer shall be initiated from the UPS Control Panel by turning the UPS inverter off.

E. Overload Ratings: The static bypass transfer switch shall have the following overload characteristics after which time a thermal protection device will engage to protect the static bypass.

1) 1000% of UPS output rating for 0.016 seconds (one cycle)

2) 150% for 30 seconds

3) 130% of UPS output rating for 1 minute

2.4.4 Microprocessor Controlled Logic

The full UPS operation shall be provided through the use of microprocessor controlled logic.  All operation and parameters are firmware controlled, thus eliminating the need for manual adjustments or potentiometers.  The logic shall include a self-test and diagnostic circuitry such that a fault can be isolated down to the printed circuit assembly or plug-in power assembly level. Every printed circuit assembly or plug-in power assembly shall be monitored.  Diagnostics shall be performed via a PC through the local diagnostics port on the UPS. 

2.4.5 Standard Communication Panel


The UPS will include a standard easy to use communication panel.  Included will be a backlit, color graphic animated LCD display, LED’s and audible indicators for UPS On line, UPS fault, UPS on battery and UPS off line.  The UPS communication panel will include UPS “ON” and UPS “OFF” pushbuttons that will permit the user to safely command the UPS on or off without risk of load loss. 

3.0 System controls and Indicators

A. Front Panel LCD Display: The UPS control panel shall provide a back-lit, color graphic display with choice of over 15 operating languages for indication of UPS status, metering, battery status, alarm event log and advanced operational features. The display provides access to:

· An animated, color mimic diagram indicating UPS power flow

· Measurements, status indications and events

· Bar-graphs and waveforms of the measured values

· Personalization menu protected by a password, used to make specific settings

· Event log with time stamping

· Access to all measurements 

System Parameters Monitored (data displayed): The visual display will display the following system parameters based on true RMS metering: 

Measurements
· Input voltage (Ph-Ph)

· Input current per phase

· Bypass voltage

· Bypass input frequency

· UPS output voltage (Ph-Ph and Ph-N) 
(3 phase simultaneously)

· UPS output current per phase
            (3 phase simultaneously)

· UPS output frequency

· UPS output % load

· UPS output kVA

· UPS out put power factor

· DC voltage

· Crest factor

· Battery current

· Battery backup time and remaining service life

· Battery temperature

Status indications and events
· Load on battery

· Load on UPS

· Load on automatic bypass

· Low-battery warning

· General alarm

· Battery fault

· Remaining back-up time during operation on battery power

· Internal fan failure

· Bypass source outside tolerances

· Battery temperature

· Additional indications shall provide maintenance assistance 

Display of operating curves: The graphical display shall be capable of displaying curves and bar graphs of the above-mentioned measured values for significant periods.

Time-stamped historical events: This function shall time-stamp and store all important status changes, anomalies and faults and make this information available for automatic or user-requested consultation; it shall interpret the events and indicate remedial measures if applicable. 

B. LED Status Indicators: The UPS control panel shall provide three LED’s that signal the following status conditions:

· Green LED: Load protected

· Yellow LED: minor fault

· Red LED: major fault, load not protected

C. On/Off switch: The UPS shall provide the ON and OFF buttons to start and stop the inverter. The switch shall provide a built-in time delay to eliminate the risk of inadvertent operation (must be pressed for 3 seconds). It is possible to remotely active the OFF function via an isolated dry contact to create an emergency power off function, resulting in:

· Inverter shutdown

· Opening of the automatic bypass

· Opening of the battery circuit breaker

· Opening of the isolated dry contact on the programmable relay card

D. Audible Alarm Reset: The UPS shall provide an audio alarm that can be stopped using the user interface.  If a new alarm is sensed after the original alarm has been silenced, it will reactivate the audible alarm. 

E. Emergency Power Off (EPO): The UPS shall be equipped with a local emergency power off button and dry contact input that can be used to command UPS shut down remotely. Activation of this command shall lead to the following actions: 
· inverter shutdown

· opening of the static bypass switch and the battery circuit breaker

· opening of an isolated dry contact on the programmable relay board

F. DB-9 Connector: One DB-9 connector with serial output will be provided for field diagnostic actions.

G. Dry Contacts: The UPS shall be provided standard with a programmable input/output relay board. This board shall have 8 dry contacts, i.e. 6 for input signals and 2 for output signals.Contacts shall be programmed as: 

· UPS on Line

· Load on Bypass

· UPS on Battery

· UPS Battery Low

· General alarm

· Remote UPS on (input)

· Remote UPS off (input)


The contacts will be normally open and will change state to indicate the operating status.  The contacts will be rated at 2.0 A (250 VDC / 30 VDC).

H. Audible Alarm Reset Touch Button: This button is used to stop the audio alarm. If a new alarm condition is detected after the button is pressed, the buzzer is reactivated.
3.1 Mechanical Design AND VENTILLATION

A. Enclosure: The UPS shall be housed in a freestanding enclosure with dead front construction. The mechanical structure of the UPS shall be sufficiently strong and rigid to withstand handling and installation operations without risk. Access to UPS subassemblies shall be through the front or top. The sheet-metal elements in the structure shall be protected against corrosion by a suitable treatment, such as zinc electroplating, bichromating, epoxy paint or an equivalent.
B. Cable Access: The standard UPS available shall accommodate top and bottom entry cables. The 10 and 15 kVA Micro Cabinet version shall accommodate bottom entry cables as standard and top entry cables with the addition of an auxiliary cabinet.  

C. Cabinet Weights and Dimensions: The width of the UPS System is [      ] (in Inches) and has a maximum weight of [       ] (in lbs).

D. Ventilation and Heat Rejection: The UPS shall be designed for forced air-cooling.  Air inlets shall be provided from the front bottom of the UPS enclosure.  Air exhaust shall be from the top rear portion of the unit.  Full load heat rejection is [        ] BTU /hour.

4.2 BATTERY

The UPS module shall use a valve regulated sealed lead acid heavy-duty industrial battery, designed for auxiliary power service in a UPS application.  The primary battery shall be furnish battery with impact resistant plastic case and housed in rack out containers inside the UPS module. 

A. Protection Against Deep Discharge and Self-Discharge: The UPS shall be equipped with a device designed to protect the battery against deep discharge depending on discharge conditions, with isolation of the battery by a circuit breaker. In particular, a monitoring device shall adjust the battery shutdown voltage as a function of a discharge coefficient to avoid excessive discharge at less than the rated output. A second device shall avoid self-discharge of the battery into the UPS control circuits during an extended shutdown of the UPS (over two hours).
B. Battery Self-Tests: The battery monitoring system shall be to perform the following automatic functions:

( Battery circuit checks every twelve hours

( Open-circuit battery test once a month

( Partial discharge test every three months

This self-test system shall signal faults via LED’s on the front panel or a message to remote supervision systems.
4.0 ACCESSORIES
4.2 Optional Purchase Items
A. Extended Battery Cabinet: Auxiliary battery cabinets will be available for extended battery times for the 10-30 kVA 32.75” standard UPS module cabinet. The optional battery cabinet will be a matching, bolt on cabinet of the same dimensions as the UPS.  All power wiring and control cables will be included with quick connectors to facilitate quick installation.  

B. External Control and Communications Devices

Up to three of the following control and communications devices may be installed in the UPS module. 

(a) RS232 serial communications card: The RS-232 serial communication card shall provide registers for all alarms and standard measurements available on the UPS. The port shall use an open J-BUS / ModBus protocol. 

(b) RS485 serial communications card: The RS485 serial communication card shall provide registers for all alarms and standard measurements available on the UPS. The port shall use an open J-BUS / ModBus protocol.
(c) Customer Provided Dry contacts: A second set (one set provided standard with the UPS module) of six (6) normally open dry contact outputs rated at 2.0 A (250 VDC / 30 VDC) shall be available to monitor UPS operation.  The dry contacts will close on the conditions listed below but shall be user programmable to close on preset thresholds of other user UPS parameters. 

· UPS on Line

· Load on Bypass

· UPS on Battery

· Low Battery Warning

· Battery Fault

· General Alarm
Two (2) dry contact inputs shall also be provided to turn the UPS inverter on and off remotely upon closure of the contacts. This feature may also be disabled if required. 

(d) SNMP Interface: The communications port shall accommodate an SNMP (Simple Network Management Protocol) converter to allow acquisition of all UPS status points via SNMP protocol for the purpose of monitoring the UPS via a network or direct connection to a PC. The SNMP adapter shall also allow for direct interface with a computer network via standard RJ-485 Ethernet network connection.

(e) Teleservice Automated Monitoring: Teleservice, which is a twenty-four hour-per-day, seven day-per-week remote UPS monitoring and reporting service shall be provided.  The systems shall use standard analog telephone lines (via modem) as the communication medium to transmit critical UPS data, alarms and anomalies back to a central station.  In addition, the central station shall communicate with each of the subscribing UPSs on a routine basis to check equipment status, operating conditions and all measured values. All reported anomalies and all routine interrogation data shall be accumulated for utilization in generating a quarterly customer report.
(f) IBM AS/400 Contact Kit:  The UPS shall interface with an IBM® AS400-UPS signal interface providing the following signals via dry contacts: 
· load on battery

· load on bypass

· low battery shutdown warning

· load powered by UPS
C. Network Based Power Management Software: Solution-PAC software shall facilitate the management of the UPS and servers over any point in a wide area network (WAN) or local area network (LAN). The software shall use a distributed, TCP/IP based architecture and must be SNMP manageable. To reduce the volume of network traffic the software will employ trap reception acknowledgement. The software must be capable of graceful server shutdown and management of individual or multiple servers from any point on the network, for up to 128 servers. 

D. Input Isolation Transformer: A delta zigzag input isolation transformer can be provided inside the standard UPS cabinet UPS cabinet to isolate the rectifier input and DC bus, for ungrounded DC systems. Input isolation transformers shall be standard on UPSs with input voltages other than 208 V. 

E. Distribution Panel Boards: Optional 24 or 42 pole front facing distribution panel boards will be provided with the UPS in a matching adjacent 23” wide cabinet.  The panel board will be a Square D, NQO panel accommodating 10-100 amp breakers.  Panel boards will accommodate any combination of one, two or three pole breakers and shall have a submain circuit breaker feeding the panel board. 

F. Two or Three Circuit Breaker Wall Mounted External Maintenance Bypass: The maintenance bypass option provides for two (2) or three (3) circuit breakers mounted inside a wall mounted enclosure to provide a wrap around bypass configuration for total UPS isolation during maintenance.  Maintenance bypass transfers shall be without interruption and kirk-key interlocked to protect the UPS from damage in the event of out of sequence transfers.
G. Two or Three Circuit Breaker External Maintenance Bypass in Matching Cabinet: The maintenance bypass option provides for two (2) or three (3) circuit breakers mounted in a matching, adjacent 23” cabinet to provide a wrap around bypass configuration for total UPS isolation during maintenance.  Maintenance bypass transfers shall be without interruption and kirk-key interlocked to protect the UPS from damage in the event of out of sequence transfers.

H. Seismic Anchors: Seismic anchors shall be available for all the UPS system cabinets. 

I. Dual Input: A second input terminal block shall be provided to accommodate a separate input source.

5.0 FIELD QUAILTY CONTROL & SERVICE ORGANIZATION

4.2 FIELD SERVICE ENGINEER QUALIFICATIONS
The manufacturer must employ a 7 X24 nation wide (international where applicable) field service organization with rapid access to all regions of the nation. The responding service professionals must be factory-trained engineers with an accredited and proven competence to service three phase UPS systems.

4.0 SPARE PARTS

Field Engineers must have immediate access to recommended spare parts with additional parts storage located in regional depots. Additional spare parts shall be accessible on a 7 x 24 basis from the national depot and must be expedited on a next available flight basis or via direct courier (whichever mode is quickest). 

4.0 MAINTENANCE TRAINING 

The manufacturer shall make available to the customer various levels of training ranging from basic UPS operation to UPS maintenance. 

4.0 MAINTENANCE & SERVICE CONTTRACTS
The manufacturer shall offer additional preventative maintenance and service contracts covering both the UPS system and the battery bank. Accredited professional service engineers, employed exclusively in the field of critical power systems service shall perform all maintenance and service. The manufacturer shall also offer extended warranty contracts. 

END OF SECTION

Specification Key

- Do noT include with final specification -

2.2 A –1
Output Power Ratings

· 10 kVA/8 kW    

· 15 kVA/12 kW
  

· 20 kVA/16 kW
(not available in23” Micro Cabinet)

· 30 kVA/24 kW
(not available in23” Micro Cabinet)
2.2 A-2 / A-3
Input / Output Voltages

· 208 VAC

· 220 VAC

· 480 VAC

· 600 VAC
2.2 A-5 
BATTERY BACK-UP TIME 


(minutes)

configuration
Battery
10kVA
15kVA
20kVA
30kVA

20 x 20 Ah
NPX-80
11
7
-
-

20 x 40 Ah
NPX-150
39
22
15
8

20 x 50 Ah
UPS12-200FR
60
35
24
12

20 x 75 Ah
UPS12-270FR

55
38
21








2.2 B-2

Input Currents


10 kVA
15 kVA
20 kVA
30 kVA

A @ 208 VAC
31
46
61
91

A @ 220 VAC
31
46
61
91

A @ 480 VAC
14
21
28
42

A @ 600 VAC
11
17
22
33

2.2 D-2 
DC Current 

12 kVA
15 kVA
20 kVA
30 kVA

ADC
49
74
97
146

4.2 C

UPS MODULE WEIGHTS AND DIMENSIONS

WIDTH (Inches)/ WEIGHT (Lbs.)

KVA

(input / output V)
10/15 kVA

208/208

Micro Cabinet
10/15 kVA

208/208


10/15 kVA

220/208

480/208

600/208
10/15 kVA

220/220

480/480

600/600
20/30 kVA

208/208


20/30 kVA

220/208

480/208

600/208
20/30 kVA

220/220

480/480

600/600

Height
48.5
62.4
62.4
62.4
62.4
62.4
62.4

Width
23
32.75
32.75
56.5
32.75
32.75
56.5

Depth
33.5
35.5
35.5
35.5
35.5
35.5
35.5

Weight
780
1434
1723
2023
1439
1839
2239


* The electrical room versions for the 10 and 15 kVA Micro Cabinet models require an additional top feed enclosure.

4.2 D

UPS MODULE HEAT REJECTION


BTU/HR

(Input / Output V)

kVA
208/208
480/208 

600/208
220/220

480/480

10kVA/8kW
4777
5800
6824

15kVA/12kW
7165
8871
10235

20kVA/16kW
8871
10918
12965

30kVA/24kW
13306
16377
19447

MGE UPS SYSTEMS - Galaxy 3000 Specification Version 1.0
1



02/03/03









